## With_0.25in
| Gas Release Event Summary |  |  | Component(s) | Toxic/ Flammable/ Inert | Mole Fraction | MW | Mass | Mass Fraction | Total Quantity Released (kg) | Qty Released in 1 hour (kg) | Tier 1 TQ (kg) | Tier 2 TQ (kg) | % of Tier 1 TQ | % of Tier 2 TQ | Total Flammable Qty Released (SCF) | Flammable Quantity Released in 1 hour (SCF)
| Facility: | Central |  | Nitrogen | Inert | 0 | 28 | 0 | 0 | 0 | 0 | 2000 | 200 | 0% | 0% | - | -
| Event Date: | 2025-02-15 |  | Hydrogen Sulfide | Toxic | 0 | 34.1 | 0 | 0 | 0 | 0 | 25 | 2.5 | 0% | 0% | - | -
| Calc. Date: | 2025-02-15 |  | Carbon Dioxide | Inert | 0 | 44 | 0 | 0 | 0 | 0 | 2000 | 200 | 0% | 0% | - | -
| By: | Krishnaraj Sambath |  | Methane | Flammable | 0.75 | 16.04 | 12.03 | 0.52826 | 10.139 | 2.7403 | 500 | 50 | 0.5481% | 5.481% | 528.5678 | 142.8562
| Indoor/Outdoor: | Outdoor |  | Ethane | Flammable | 0.12 | 30.07 | 3.6084 | 0.15845 | 3.0412 | 0.82194 | 500 | 50 | 0.1644% | 1.644% | 84.5709 | 22.857
| Total quantity released: | 0.70476 | MCF | Propane | Flammable | 0.07 | 44.09 | 3.0863 | 0.13552 | 2.6012 | 0.70302 | 500 | 50 | 0.1406% | 1.406% | 49.333 | 13.3332
| Release duration: | 222 |  | Butane | Flammable | 0.03 | 58.12 | 1.7436 | 0.076564 | 1.4695 | 0.39717 | 500 | 50 | 0.07943% | 0.7943% | 21.1427 | 5.7142
| % Combusted | 0% |  | Pentane | Flammable | 0.02 | 72.15 | 1.443 | 0.063365 | 1.2162 | 0.3287 | 500 | 50 | 0.06574% | 0.6574% | 14.0951 | 3.8095
|  |  |  | Hexane | Flammable | 0.01 | 86.17 | 0.8617 | 0.037839 | 0.72625 | 0.19628 | 1000 | 100 | 0.01963% | 0.1963% | 7.0476 | 1.9047
| Flowrate in 1 hr: | 5.1874 | (See Note 1) | Heptane | Flammable | 0 | 100.2 | 0 | 0 | 0 | 0 | 1000 | 100 | 0% | 0% | 0 | 0
| Qty released in 1 hr: | 5.1874 |  | Octane | Flammable | 0 | 114.22 | 0 | 0 | 0 | 0 | 1000 | 100 | 0% | 0% | 0 | 0
|  |  |  | Sum: |  | 1 |  | 22.773 | 1 | 19.1933 | 5.1874 |  |  | 1.018% | 10.18% | 704.7571 | 190.4749
During total duration | Total quantity released (in volume): | 0.70476 | (See Note 2)
| Total quantity released (in mass): | 19.1933 |  |  |  | Note 1: | Override C11 if worst hour release rate is available and different
| Unburnt gas (in volume) | 0.70476 |  | Key |  | 2023 OEDRS
| Unburnt gas (in mass) | 19.1933 |  | Inputs
Interim Calcs
In one-hour period | Quantity released in 1 hr (in volume): | 0.19047 |  | Outputs
| Quantity released in 1 hr (in mass): | 5.1874
| Unburnt gas (in volume) | 0.19047
| Unburnt gas (in mass) | 5.1874
Category | Tier 1 | Tier 2
Toxic | 0% | 0%
Flammable | 1.018% | 10.18%
Inert | 0% | 0%
Note 2:
API's 2009 GHG Compendium

## With_0.5in
| Gas Release Event Summary |  |  | Component(s) | Toxic/ Flammable/ Inert | Mole Fraction | MW | Mass | Mass Fraction | Total Quantity Released (kg) | Qty Released in 1 hour (kg) | Tier 1 TQ (kg) | Tier 2 TQ (kg) | % of Tier 1 TQ | % of Tier 2 TQ | Total Flammable Qty Released (SCF) | Flammable Quantity Released in 1 hour (SCF)
| Facility: | Central |  | Nitrogen | Inert | 0 | 28 | 0 | 0 | 0 | 0 | 2000 | 200 | 0% | 0% | - | -
| Event Date: | 2025-02-15 |  | Hydrogen Sulfide | Toxic | 0 | 34.1 | 0 | 0 | 0 | 0 | 25 | 2.5 | 0% | 0% | - | -
| Calc. Date: | 2025-02-15 |  | Carbon Dioxide | Inert | 0 | 44 | 0 | 0 | 0 | 0 | 2000 | 200 | 0% | 0% | - | -
| By: | Krishnaraj Sambath |  | Methane | Flammable | 0.75 | 16.04 | 12.03 | 0.52826 | 10.139 | 10.139 | 500 | 50 | 2.028% | 20.28% | 528.5678 | 528.5678
| Indoor/Outdoor: | Outdoor |  | Ethane | Flammable | 0.12 | 30.07 | 3.6084 | 0.15845 | 3.0412 | 3.0412 | 500 | 50 | 0.6082% | 6.082% | 84.5709 | 84.5709
| Total quantity released: | 0.70476 | MCF | Propane | Flammable | 0.07 | 44.09 | 3.0863 | 0.13552 | 2.6012 | 2.6012 | 500 | 50 | 0.5202% | 5.202% | 49.333 | 49.333
| Release duration: | 52 |  | Butane | Flammable | 0.03 | 58.12 | 1.7436 | 0.076564 | 1.4695 | 1.4695 | 500 | 50 | 0.2939% | 2.939% | 21.1427 | 21.1427
| % Combusted | 0% |  | Pentane | Flammable | 0.02 | 72.15 | 1.443 | 0.063365 | 1.2162 | 1.2162 | 500 | 50 | 0.2432% | 2.432% | 14.0951 | 14.0951
|  |  |  | Hexane | Flammable | 0.01 | 86.17 | 0.8617 | 0.037839 | 0.72625 | 0.72625 | 1000 | 100 | 0.07262% | 0.7262% | 7.0476 | 7.0476
| Flowrate in 1 hr: | 19.1933 | (See Note 1) | Heptane | Flammable | 0 | 100.2 | 0 | 0 | 0 | 0 | 1000 | 100 | 0% | 0% | 0 | 0
| Qty released in 1 hr: | 19.1933 |  | Octane | Flammable | 0 | 114.22 | 0 | 0 | 0 | 0 | 1000 | 100 | 0% | 0% | 0 | 0
|  |  |  | Sum: |  | 1 |  | 22.773 | 1 | 19.1933 | 19.1933 |  |  | 3.766% | 37.66% | 704.7571 | 704.7571
During total duration | Total quantity released (in volume): | 0.70476 | (See Note 2)
| Total quantity released (in mass): | 19.1933 |  |  |  | Note 1: | Override C11 if worst hour release rate is available and different
| Unburnt gas (in volume) | 0.70476 |  | Key |  | 2023 OEDRS
| Unburnt gas (in mass) | 19.1933 |  | Inputs
Interim Calcs
In one-hour period | Quantity released in 1 hr (in volume): | 0.70476 |  | Outputs
| Quantity released in 1 hr (in mass): | 19.1933
| Unburnt gas (in volume) | 0.70476
| Unburnt gas (in mass) | 19.1933
Category | Tier 1 | Tier 2
Toxic | 0% | 0%
Flammable | 3.766% | 37.66%
Inert | 0% | 0%
Note 2:
API's 2009 GHG Compendium

## VolumeCalcs
Volume Type | D2 [in] | D1 [in] | hL [in] | L [ft] | th_1 | Vliq_Cyl | Vliq_Caps | V_tot | Vol. [ft3] | Pinitial [psig] | Pfinal [psig] | T [F] | Z_LP | Z_HP | Zinitial | Z_LP | Z_HP | Zfinal | Release [MCF] | Legend
Pipe | 0 | 6 | 0 | 1000 | 0 | 0 | 0 | 196.3823 | 196.3495 | 60 | 5 | 90 | 0.9872 | 0.3867 | 0.9872 | 0.99893 | 0.38056 | 0.99893 | 0.70476 |  | Input
Please select the volume type that best resembles the equipment that was blown down | [20 empty] | Ignored
Interim Calcs
Output
Method:
Based on non-ideal gas law (PV = ZnRT), number of moles in the pipeline before and after the event is computed
The difference is converted to MCF for release estimate
Approach:
If Release Volume is greater than 100 MCF, reach out to process engineering team for verification
Detailed HYSYS simulations may be performed for additional / independent review
Notes:
If T_Gas [F] is unavailable, use 60F for a conservative estimate
Above method is validated for 0 < P < 5000 psig, 40 < T < 150 F
If (P, T) for your scenario is outside this range, please contact proces engineering team
Refer to chapter 3 of AVENGERS playbook (by process engineering) for further details

## Examples
Volume Type | D2 [in] | D1 [in] | hL [in] | L [ft] | th_1 | Vliq_Cyl | Vliq_Caps | V_tot | Vol. [ft3] | Pinitial [psig] | Pfinal [psig] | T [F] | Z_LP | Z_HP | Zinitial | Z_LP | Z_HP | Zfinal | Valve Size [in] | Duration [s] | Release [MCF]
Sep. Vessel | 0 | 96 | 0 | 30 | 0 | 0 | 0 | 1642.0058 | 1642.0058 | 100 | 5 | 90 | 0.97867 | 0.39117 | 0.97867 | 0.99893 | 0.38056 | 0.99893 | 0.25 | 31024 | 10.2687
Pipe | 0 | 4 | 9.6 | 5280 | #NUM! | #NUM! | -0.10053 | 460.7766 | 460.7669 | 1100 | 5 | 90 | 0.76533 | 0.50283 | 0.76533 | 0.99893 | 0.38056 | 0.99893 | 0.3 | 25128 | 42.4714
Annulus | 3 | 5 | 9.6 | 11200 | #NUM! | #NUM! | -0.058643 | 1527.182 | 977.3844 | 3000 | 50 | 90 | 0.36 | 0.715 | 0.715 | 0.98933 | 0.38558 | 0.98933 | 0.25 | 66054 | 260.2815
Legend
Input
Ignored
Interim Calcs
Output
Method:
Based on non-ideal gas law (PV = ZnRT), number of moles in the pipeline before and after the event is computed
The difference is converted to MCF for release estimate
Approach:
If Release Volume is greater than 100 MCF, reach out to process engineering team for verification
Detailed HYSYS simulations may be performed for additional / independent review
Notes:
If T_Gas [F] is unavailable, use 60F for a conservative estimate
Above method is validated for 0 < P < 5000 psig, 40 < T < 150 F
If (P, T) for your scenario is outside this range, please contact proces engineering team
Refer to chapter 3 of AVENGERS playbook (by process engineering) for further details